Datasheet

AIO-422-R1 Module

Part No. 0000007

# Product Description

The AIO-422-R1 is a high-precision analog I/O expansion module designed for home automation, HVAC, and environmental monitoring. It connects to MicroPLC or MiniPLC controllers via RS-485 (Modbus RTU) and integrates with ESPHome and Home Assistant for analog sensing and control in smart automation systems.

Typical use includes real-time analog signal monitoring, analog output automation (lighting, HVAC, pumps), accurate temperature-based triggers using RTDs, and custom automation logic via MQTT or native ESPHome entities.

# Technical Specifications

| Specification | Details |
| --- | --- |
| Power supply | 24 V DC |
| Power consumption (typical) | Not specified. |
| Power consumption (max) | Not specified. |
| MCU | RP2350A (from previous datasheet). |
| Analog inputs | 4 × 0–10 V (ADS1115, 16-bit) |
| Analog outputs | 2 × 0–10 V (MCP4725, 12-bit) |
| RTD inputs | 2 × PT100/PT1000 (MAX31865); 2-, 3-, or 4-wire |
| Input/Output protection | ESD, overvoltage |
| Communication interface | RS-485 (Modbus RTU); half-duplex, up to 115.2 kbps, with protections (from previous datasheet). |
| USB port | USB Type-C; USB 2.0, CP2102N, ESD protection (from previous datasheet). |
| RTC | PCF8563 (from previous datasheet). |
| User interface | 4 front-panel buttons, status LEDs |
| Dimensions | DIN-rail, 3 modules wide; 52.5 × 90 × 59 mm, 9 division units (from previous datasheet). |
| Compatibility | MicroPLC, MiniPLC |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type / pitch | 5.08 mm pitch (from previous datasheet). |
| Terminal Specifications | Wire cross-section / rating | 300 V, 20 A; 26–12 AWG (from previous datasheet). |
| Terminal Specifications | Tightening torque | 0.5–0.6 Nm (from previous datasheet). |
| Environmental Ratings | Operating temperature | 0 °C to +40 °C (from previous datasheet). |
| Environmental Ratings | Relative humidity | Max 95 % RH, non-condensing (from previous datasheet). |
| Environmental Ratings | Ingress protection | IP20 (from previous datasheet). |
| Mechanical & Packaging | Product dimensions | 52.5 × 90 × 59 mm (from previous datasheet). |
| Mechanical & Packaging | DIN units | 9 division units (from previous datasheet). |
| Mechanical & Packaging | Mounting | DIN rail per EN 50022, 35 mm (from previous datasheet). |
| Mechanical & Packaging | Materials / finish | Not specified. |
| Mechanical & Packaging | Net weight | Not specified. |

# Compliance & Certifications

IP20.

Operation Type 1 (UL60730-1, CSA E60730-1).

Rated impulse voltage for digital output: 2.5 kV (UL60730-1, altitude ≤ 2000 m).

Degree of pollution: 2.

Certifications: CE, UL60730-1, CSA E60730-1 (from previous datasheet).

Notes: Compliance statements above are from the previous datasheet (PDF). README does not specify certifications or compliance; no conflict identified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu