Datasheet

ALM-173-R1 Module for Alarm Systems

Part No. TBD

# Product Description

The ALM-173-R1 is a configurable alarm I/O module for intrusion detection, fault annunciation, and local supervision. It integrates with a MicroPLC/MiniPLC or any Modbus master over RS-485 (Modbus RTU) and is configured via a USB-C WebConfig UI (Web Serial). - I/O: 17 opto-isolated digital inputs, 3 SPDT relays

# Technical Specifications

| Specification | Details |
| --- | --- |
| Digital Inputs | 17; Dry contact / isolated LV; per-input Enable, Invert, debounce, Group (1/2/3) |
| Relays | 3 (SPDT); Follow alarm Group, Master (Modbus), or Manual Override; invert/enable per channel |
| Alarm Groups | 3 + Any; Modes: Active-while (momentary) or Latched-until-ack |
| User Buttons | 4; Ack All, Ack G1–G3, or Relay 1–3 override |
| User LEDs | 4; Steady/Blink; sources: Any, G1–G3, or Relay override |
| Config UI | —; WebConfig via USB-C (Web Serial): Modbus addr/baud, mapping, live status, reset |
| Modbus RTU | RS-485; Multi-drop slave; Address 1–255, 9600–115200 baud |
| MCU | RP2350 + QSPI; Dual-core MCU with external flash; resilient field I/O control |
| Power | 24 VDC; 24→5→3.3 V regulators + isolated sensor rails (+12 V, +5 V) |
| Protection | —; TVS, PTC, and ESD protection on field connections |
| Digital Inputs (IN1…IN17) | 17; Opto-isolated to GND_ISO; dry contact / isolated LV; debounce/invert/group in firmware. |
| Relays (RLY1…RLY3) | 3; SPDT COM/NO/NC; can follow alarm groups, master, or manual override. |
| Isolated Sensor Rails | 2; +12 V (PS/1), +5 V (PS/2); isolated & fuse-limited (sensors only). |
| Field Bus | 1; RS-485 A/B/COM with protection and fail-safe bias. |
| Service | 1; USB-C (config/diagnostics). |
| Supply (V+) | 20 V / 24 V / 30 V / SELV, protected input |
| Power (module) | — / 1.85 W / 3.0 W / No external loads |
| Relays (contacts) | — / — / — / 250 VAC 16 A (cosφ=1), 30 VDC 10 A; derate for inductive |
| RS-485 speed | — / — / 115.2 kbps / 8N1 |
| Operating temp | 0 °C / — / 40 °C / ≤95% RH, non-condensing |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type / pitch | terminals** are torqued and strain-relieved |
| Environmental Ratings | Operating temperature | Operating temp |
| Environmental Ratings | Ingress protection | IP20 |
| Environmental Ratings | Relative humidity | 95% RH |
| Mechanical & Packaging | Product dimensions | 157.4 × 91 × 58.4 mm |
| Mechanical & Packaging | Mounting | EN 50022 |
| Mechanical & Packaging | Net weight | 420 g |

# Compliance & Certifications

ce

ee

ce

ce

CE

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ee

ce

ce

ee

ee

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ee

ee

ee

ce

ce

ce

ee

ee

ee

ce

ce

ee

ce

ee

ee

ce

ce

ee

ce

ee

ee

ce

ce

ce

ce

ce

ee

ce

ce

ee

ce

ce

ce

ce

ee

ce

ee

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

EE

ce

ce

ce

ce

CE

ce

ee

ce

ee

ee

ee

ce

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu