# ALM-173-R1 Module for Alarm Systems

DIN rail • 24 V DC • Modbus RTU • Home Assistant

# Overview

The **ALM-173-R1** is a configurable **alarm I/O module** for **intrusion detection**, **fault annunciation**, and **local supervision**. It integrates with a **MicroPLC/MiniPLC** or any Modbus master over **RS-485 (Modbus RTU)** and is configured via a USB-C **WebConfig** UI (Web Serial).

**Highlights**

**I/O:** **17 opto-isolated digital inputs**, **3 SPDT relays**

**Local HMI:** **4 buttons** (ack/override) and **4 LEDs** (status/alert)

**Interface:** RS-485 (Modbus RTU), address **1–255**, **9600–115200** baud

**Setup:** Web browser (Chromium) via USB-C **WebConfig**; live status + safe **device reset**

**Design:** **Galvanically isolated** field side; **RP2350 MCU** with **MAX485** and **PCF8574** expanders; powered from **24 VDC**

**Integration:** Modbus map exposes inputs, alarm/group bits, and relay states (works smoothly with **Home Assistant** / PLC / SCADA)

**Quick use case:** wire inputs → assign to alarm groups → choose **Active-while** or **Latched-until-ack** → map groups to relays/LEDs → connect RS-485 → acknowledge locally or via Modbus.

# Quick Overview

| Subsystem | Qty | Description |
| --- | --- | --- |
| **Digital Inputs** | 17 | Dry contact / isolated LV; per-input **Enable**, **Invert**, debounce, **Group (1/2/3)** |
| **Relays** | 3 (SPDT) | Follow alarm **Group**, **Master (Modbus)**, or **Manual Override**; invert/enable per channel |
| **Alarm Groups** | 3 + Any | Modes: **Active-while** (momentary) or **Latched-until-ack** |
| **User Buttons** | 4 | **Ack All**, **Ack G1–G3**, or **Relay 1–3 override** |
| **User LEDs** | 4 | Steady/Blink; sources: **Any**, **G1–G3**, or **Relay override** |
| **Config UI** | — | **WebConfig** via USB-C (Web Serial): Modbus addr/baud, mapping, live status, reset |
| **Modbus RTU** | RS-485 | Multi-drop slave; **Address 1–255**, **9600–115200** baud |
| **MCU** | RP2350 + QSPI | Dual-core MCU with external flash; resilient field I/O control |
| **Power** | 24 VDC | 24→5→3.3 V regulators + **isolated sensor rails** (+12 V, +5 V) |
| **Protection** | — | **TVS**, **PTC**, and ESD protection on field connections |

# Typical Applications

These are practical examples of deploying the **ALM-173-R1** with the HomeMaster Mini/Micro PLC or any Modbus RTU master.

Each case uses built-in firmware features via the Web Serial UI:

**Input settings:** Enable, Invert, Group

**Relay logic:** Enable, Invert, Group or Manual

**Alarm behavior:** Latched or Momentary

**Buttons & LEDs:** Ack / Override / Status

**Modbus:** PLC reads status and controls relays

---

## 1) [Intrusion] Zone Alarm with Siren (Latched)

**Trigger a siren when a sensor activates. Alarm stays ON until acknowledged.**

**Steps:**

Map **IN1 → Group 1**; enable + invert if NC.

Set **Group 1 → Latched until acknowledged**.

Map **Relay 1 → Group 1** (enable; invert if required).

Set **Button 1 → Acknowledge Group 1**.

Set **LED 1 → Group 1, Blink mode**.

PLC reads Group 1 + “Any Alarm” status.

---

## 2) [Access Control] Dual-Door Alarm with Shared Strobe

**Two zones, each with own buzzer. Common strobe flashes on any alarm.**

**Steps:**

Map **IN1 → Group 1**, **IN2 → Group 2**.

Set **Groups 1 & 2 → Latched**.

Map **Relay 1 → Group 1**, **Relay 2 → Group 2**.

PLC toggles **Relay 3** when “Any Alarm” is active.

Set **Button 1 → Ack G1**, **Button 2 → Ack G2**.

Set **LEDs 1–3 → G1, G2, Any Alarm**.

---

## 3) [Supervision] Equipment Room Summary Alarm

**Aggregate faults (smoke, thermal, flood, etc.) into one visual + Modbus alarm.**

**Steps:**

Map **IN1–IN8 → Group 1**, invert per sensor.

Set **Group 1 → Active while condition is active**.

Map **Relay 1 → Group 1** (to stack light).

Set **LED 1 → Any Alarm, Blink**.

PLC reads **Any** and **Group 1** status.

---

## 4) [Access Control] Door Strike with Timeout Alarm

**PLC unlocks door, monitors contact, alarms if left open too long.**

**Steps:**

Map **IN1 → Group 3** (Invert if NC).

Leave **Relay 1 = Group None**; PLC controls strike directly.

In PLC logic: if **IN1** open too long → set **Group 3** or energize **Relay 2**.

Set **Button 4 → Ack Group 3**, **LED 3 → Group 3**.

---

## 5) [Annunciator Panel] Any Alarm Indication

**Use the front panel to show system-wide or per-group alarm state.**

**Steps:**

Map inputs **IN1…INn → Group 1–3**.

Set groups to either **Latched** or **Active while** depending on use.

Set **LED 1 → Any Alarm, Blink**

Set **LED 2 → Group 1**, **LED 3 → Group 2**, **LED 4 → Group 3**

PLC mirrors lamp states to HMI/HA dashboard.

---

> 💡 **Tip:** “Any Alarm” is always available via Modbus and can be mapped to a summary relay or LED.

# Tech Specs

See module README for details.

# Installation, Environmental & Mechanical

**DIN-rail:** EN 50022, 35 mm; **PC/ABS V-0** enclosure

**Size / mass:** **157.4 × 91 × 58.4 mm**, ~**420 g**

**Dimensions drawing:**

**Environmental:** **IP20**, Type 1; impulse 2.5 kV; altitude ≤ 2000 m; pollution degree 2

# Home Assistant & ESPHome Integration

The **ALM-173-R1** joins your system over **RS-485 (Modbus RTU)**. Setup has two parts:

1) **Physical wiring**, 2) **Digital configuration** (WebConfig → optional ESPHome/PLC).

---

# Documentation

The following key project resources are included in this repository:

**🧠 Firmware (Arduino/PlatformIO):** `Firmware/default_alm_173_r1/`

Main sketch implementing relays, button overrides, alarms, Modbus RTU, and WebSerial support.

**🛠 Web Config Tool:** `Firmware/ConfigToolPage.html`

HTML‑based USB Web Serial configuration UI, used for meter options, calibration, relays, alarms, etc.

**📷 Images & Visual Documentation:** `Images/`

Contains UI screenshots, module photos, diagrams, and layout references used in this documentation.

**📐 Hardware Schematics:** `Schematics/`

Includes Field Board and MCU Board schematics in PDF format for hardware developers and integrators.

**📖 Datasheet & Documentation (if available):** `Manuals/`

Contains PDF datasheets or technical overviews, if applicable.

# Power Supply

Ensure the following before applying power:

[ ] **All terminals** are torqued and strain-relieved

[ ] No accidental bridges between **logic ground** and **GND_ISO**

[ ] Relays are correctly wired (**COM/NO/NC**) with snubbers installed

[ ] RS-485 **A/B polarity and termination** are correct

[ ] Sensor current on **PS/1 (12 V)** and **PS/2 (5 V)** is within limits

---

# Inputs & Outputs

| Interface | Qty | Electrical / Notes |
| --- | --- | --- |
| **Digital Inputs (IN1…IN17)** | 17 | Opto-isolated to **GND_ISO**; dry contact / isolated LV; debounce/invert/group in firmware. |
| **Relays (RLY1…RLY3)** | 3 | SPDT **COM/NO/NC**; can follow alarm groups, master, or manual override. |
| **Isolated Sensor Rails** | 2 | **+12 V (PS/1)**, **+5 V (PS/2)**; isolated & fuse-limited (sensors only). |
| **User Buttons** | 4 | Ack All / Ack G1–G3 / Relay overrides (configurable). |
| **User LEDs** | 4 (+PWR/TX/RX) | Map to Any/G1–G3/Overrides; Steady/Blink; TX/RX show bus activity. |
| **Field Bus** | 1 | RS-485 **A/B/COM** with protection and fail-safe bias. |
| **Service** | 1 | **USB-C** (config/diagnostics). |

# Cable Recommendations & Shield Grounding

## 🔌 Power

| Area | Warning |
| --- | --- |
| **24 VDC Input** | Use a **clean SELV** 24 VDC source. Reverse polarity can damage the module. Fuse the supply upstream. |
| **Sensor Rails (12 V / 5 V)** | For **low-power sensors only**. Never backfeed or parallel with external rails. Short circuits may trip **PTC fuses** (auto-reset). |

## ⚠️ Inputs & Relays

| Area | Warning |
| --- | --- |
| **Digital Inputs (IN1–IN17)** | Accept **dry contacts** or isolated low-voltage signals only. Never apply high voltage. Respect debounce/invert settings in UI. |
| **Relay Outputs (RLY1–3)** | **Dry contacts** only. Do not exceed rated current/voltage. **Snub** inductive loads externally (RC/TVS). Do not route high-current return through logic ground. |

## 🧠 Communication & USB

| Area | Warning |
| --- | --- |
| **RS-485 Bus** | Use **twisted pair (shielded)**. Terminate and bias once per trunk. Protect against surges. Not designed for lightning arrest. |
| **USB-C (Front)** | For **setup only**. Never use to power field devices. During storms or if trunk is long/exposed, disconnect USB from PC. |

## 👆 Front Panel

| Area | Warning |
| --- | --- |
| **Buttons & LEDs** | Can acknowledge alarms or override relays. Disable in firmware or use protective enclosures in safety-critical environments. |

## 📶 Shielding & EMC

| Area | Recommendation |
| --- | --- |
| **Cable Shields** | Terminate at one point only (typically the controller). Keep signal wiring away from VFDs or high-energy switching circuits. |

---

# System Architecture & Pinout

| ALM System Diagram | RP2350 MCU Pinout |
| --- | --- |

| Field Board Layout | MCU Board Layout |
| --- | --- |

# ESPHome YAML Configuration & Hardware Pinout Manual

| ALM System Diagram | RP2350 MCU Pinout |
| --- | --- |

| Field Board Layout | MCU Board Layout |
| --- | --- |

# Links

**MicroPython**

**C/C++**

**Arduino IDE**