Datasheet

DIM-420-R1 — Module for Dual-Channel AC Dimming

Part No. TBD

# Product Description

The DIM-420-R1 is a configurable smart I/O module designed for dimming AC loads via leading/trailing edge phase control. It includes 4 digital inputs, 2 dimming outputs, 4 user buttons, and 4 LEDs, with configuration via WebConfig using USB-C (Web Serial).

# Technical Specifications

| Specification | Details |
| --- | --- |
| Digital Inputs | 4; isolated dry‑contact inputs (ISO1212 front‑end); modes: *Momentary*/*Latching* with Short / Long / Double / Short‑then‑Long press types. Debounced and firmware‑interpreted for actions. |
| Dimming Outputs | 2; MOSFET‑based phase‑cut AC outputs; Leading/Trailing per channel with Lower/Upper threshold limits and zero‑cross sync/monitoring. |
| Relays | 0; – |
| User LEDs | 4; Steady/Blink; sources: CH1/CH2 state, DI1–DI4, or AC presence (ZC OK). |
| User Buttons | 4; Local acknowledge/override; firmware press‑logic for toggle, ramp (ping‑pong), preset, max. |
| Config UI | Web Serial; WebConfig in Chromium browser over USB‑C; edit Modbus addr/baud, thresholds, cut mode, presets; live log & JSON snapshot. |
| Modbus RTU | RS‑485; Multi‑drop slave; FC01/05/02/03/06/16 with discrete inputs, coils, and holding registers. Defaults ID=3, 19200, 8N1. |
| MCU | RP2350A; Dual‑core MCU; QSPI flash for firmware/config; Arduino/PlatformIO supported. |
| Power | 24 VDC; Protected 24 V input; on‑board isolated 5 V rails for power stages (B2405S‑2WR3) and local 3.3 V regulation. |
| Protection | TVS, PTC; Surge/ESD protection and resettable fuses on field I/O and RS‑485/USB/power paths. |
| Role | Slave (DIM‑420‑R1) |
| Address Range | 1–247 (default = `3`) |
| Baud | 9600–115200 (default = `19200`) |
| Format | 8 data bits, No parity, 1 stop bit (8N1) |
| RS‑485 Bus | 1; Modbus RTU slave (A/B/COM) |
| USB‑C Port | 1; Configuration & firmware via Web Serial (USB) |
| Supply Voltage (V+) | 24 VDC ±10% SELV |
| Power Consumption | Typ. 1.85 W / Max. 3 W |
| Logic Rails | 5 V (Buck), 3.3 V (LDO) |
| Isolated Power Rails | +5V_ISO1 / +5V_ISO2 |
| DI Input Threshold | 24 VDC, opto-isolated (ISO1212) |
| USB-C Function | Web Serial + UF2 upload |
| RS-485 Interface | 115.2 kbps max, Modbus RTU |
| Temperature Range | 0…+40 °C |
| Humidity Range | ≤ 95 % RH, non-condensing |
| Supply voltage (V+) | 20 V / 24 V / 30 V / SELV; reverse polarity protected |
| Power consumption | – / 1.85 W / 3 W / Logic only (no load) |
| Logic rails | – / 5 V / 3.3 V / – / Buck + LDO derived |
| Isolated rails | +5V_ISO1/2 / – / – / Internal use for dimmer stage only |
| Digital inputs | – / – / 24 VDC / ISO1212 front-end, protected |
| AC dimmer outputs | – / – / 110/230 VAC / 2× WMM36N65C4 (MOSFET) |
| USB-C (setup only) | 5 V / – / – |
| Ambient temperature | 0 °C / – / +40 °C / 32–104 °F |
| Humidity (operating) | – / – / 95 %RH / Non-condensing |
| Operating Temp | 0 °C … +40 °C |
| Operating Humidity | ≤ 95 % RH, non-condensing |
| Ingress Protection | IP20 |
| Pollution Degree | 2 |
| Impulse Voltage | 2.5 kV (UL60730-1) |
| Operation Class | Type 1 (UL60730-1, CSA E60730-1) |
| Altitude Rating | ≤ 2000 m |
| Certifications | CE, UL60730-1, CSA E60730-1 |
| RoHS / Pb-free | ✅ Compliant |
| Slave ID | `3` |
| Baud Rate | `19200` |
| Framing | `8N1` |
| Protocol | Modbus RTU |
| Port | RS‑485 (A/B/COM) |
| Change via | USB-C WebConfig |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type / pitch | terminals are 5.08 mm pitch, 300 V / 20 A rated, 26–12 AWG. |
| Environmental Ratings | Operating temperature | Operating Temp |
| Environmental Ratings | Ingress protection | Ingress Protection |
| Environmental Ratings | Relative humidity | Humidity Range ¦ ≤ 95 % RH, non |
| Mechanical & Packaging | Product dimensions | 157.4 × 91 × 58.4 mm |
| Mechanical & Packaging | Mounting | 35 mm DIN |
| Mechanical & Packaging | Net weight | 1 G |

# Compliance & Certifications

ce

ee

ce

ce

CE

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ee

ce

ce

ee

ce

ee

ce

ce

ce

ee

ee

ee

ee

ee

ee

ee

ce

ee

ce

ce

ce

ce

ee

ce

ce

ce

ce

ee

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

UL60730-1

UL60730-1

CSA E60730-1)  |

Ce

CE

UL60730-1

CSA E60730-1       |

RoHS

ee

Compliant                      |

ce

ce

ce

ce

ce

ee

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

CE

ce

ce

ee

ce

ee

ee

ee

ee

ee

ee

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu