# DIM-420-R1 — Module for Dual-Channel AC Dimming

DIN rail • 24 V DC • Modbus RTU • Home Assistant

# Overview

See module README for details.

# Quick Overview

The **DIM‑420‑R1** is a modular dimmer I/O device for **dual‑channel phase‑cut AC dimming** in the **HomeMaster MicroPLC / MiniPLC** ecosystem. It exposes **2 dimming channels**, **4 isolated digital inputs**, **4 configurable user buttons**, **4 user LEDs**, and an **RS‑485 Modbus RTU** interface. Setup and diagnostics are performed in‑browser via **WebConfig over USB‑C (Web Serial)**—no special software required.

It integrates seamlessly with **MiniPLC / MicroPLC controllers, third‑party Modbus masters, ESPHome / Home Assistant, and SCADA/PLC systems**. Typical use: connect wall switches to the DIs, pick **Leading/Trailing edge** per load, set **Lower/Upper thresholds**, and control scenes from a PLC or locally with press‑logic.

**Quick use case:**

Wire DI1–DI4 to wall switches → select *Momentary* or *Latching* with Short/Long/Double logic → choose **Cut Mode** and **Load Type** per channel → map LEDs/Buttons → connect RS‑485 A/B → control and monitor via PLC / ESPHome.

---

# Typical Applications

See module README for details.

# Tech Specs

---

# Installation, Environmental & Mechanical

| Attribute | Value |
| --- | --- |
| Mounting | DIN rail (EN50022, 35 mm) |
| Material | PC/ABS, UL V-0 |
| Color / Finish | Light Gray / Smoke, Matte |
| Dimensions (L×W×H) | 157.4 × 91 × 58.4 mm |
| Division Units | 9M |
| Net Weight | 420 g |
| Terminal Specs | 26–12 AWG, 0.5–0.6 Nm torque |

---

# Home Assistant & ESPHome Integration

The **DIM‑420‑R1** is a smart dual-channel dimmer with **Modbus RTU** and onboard **USB‑C WebConfig**. Setup has two main stages:

**Wiring & power** (24 V + RS‑485 + AC load)

**Digital configuration** (WebConfig → Modbus ID, Cut Mode, etc.)

---

# Documentation

| Item | Link |
| --- | --- |
| **Firmware Source** | `/Firmware/default_DIM_420_R1` |
| **ESPHome Config** | `default_dim_420_r1_plc.yaml` |
| **WebConfig Tool** | Online Version |
| **Schematics (PDF)** | `/Schematics` |
| **Mechanical Images** | See `/Images/` in repo |
| **Datasheet** | `DIM-420-R1.pdf` |

---

<a id="12-support"></a>

# Power Supply

The DIM‑420‑R1 uses **24 VDC SELV** for logic, UI, RS‑485, and Web Serial.

AC power is handled separately by the dimming channels (see §4.4).

## 🔌 Supply Details

| Type | Description |
| --- | --- |
| **24 VDC Input** | Primary logic power. Connect `V+` / `0V`. Protected by fuse + TVS. |
| **AC Power** | CH1/CH2 output sections are powered via `Lx_IN/Nx_IN` terminals. **Do not share logic power and AC domains.** |
| **Internal Rails** | Onboard 5 V + 3.3 V (buck-regulated) for logic, UI, and isolated side. |

## ⚡ Current

~50 mA idle (logic + UI only)

Add budget if using all 4 LEDs, buttons, and rapid RS‑485 comms.

AC loads pull from **separate mains lines** — never through the 24 V rail.

---

# Inputs & Outputs

| Interface | Qty | Description |
| --- | --- | --- |
| **Digital Inputs** | 4 | Opto-isolated sourcing inputs, surge-protected |
| **Dimming Outputs** | 2 | Phase-cut AC outputs (MOSFET, Leading/Trailing) |
| **User Buttons** | 4 | Local override / toggle / ramp / preset actions |
| **User LEDs** | 4 | Configurable (CH state, AC presence, DI state) |
| **RS‑485 Bus** | 1 | Modbus RTU slave (A/B/COM) |
| **USB‑C Port** | 1 | Configuration & firmware via Web Serial (USB) |
| **Relays** | 0 | Not present (uses solid-state AC dimming) |

---

# Cable Recommendations & Shield Grounding

## Power

| Area | Warning |
| --- | --- |
| **24 VDC Input** | Use a **clean SELV 24 VDC** source; observe polarity. Protected by fuses/TVS and buck → 5 V/3.3 V regulators. |
| **Isolated Rails** | `+5V_ISO1/ISO2` feed the dimmer power stages; they belong to the **mains domain**. Do **not** use for external sensors. |

## Inputs (SELV)

| Area | Warning |
| --- | --- |
| **DI1–DI4** | **Dry contacts / isolated low‑voltage** only (isolated front end). Do **not** apply mains. Use `DIx_GND` returns and configure debounce/invert in UI. |

## Dimming Channels (MAINS)

| Area | Warning |
| --- | --- |
| **CH1 / CH2 AC Terminals** | `Lx_IN/Lx_OUT, Nx_IN/Nx_OUT` carry **hazardous mains**. Use appropriate insulation, creepage/clearance, and enclosure practices. Components include HV MOSFETs (**650 V class**) and opto interfaces. |
| **Load Types** | Use loads compatible with selected **Leading/Trailing** edge. Many LED drivers require Trailing; check the datasheet. |
| **Snubbers/EMI** | Internal suppression is provided in the power stage; add external RC snubbers only if the load manufacturer requires it. Keep mains wiring short and twisted where possible. |

## Communication & USB (SELV)

| Area | Warning |
| --- | --- |
| **RS‑485 (A/B/COM)** | Use twisted pair (shielded). Terminate at bus ends (≈120 Ω). Maintain SELV separation from AC wiring. |
| **USB‑C (setup only)** | For configuration/UF2 only. Avoid connecting a PC to the USB port while panels are open and mains wiring is exposed; mind ground loops. |

---

## ✅ Pre‑Power Checklist

All **AC and SELV** cables are routed separately with strain relief.

No bridges between **logic GND** and **GND_ISO1/2**; isolation gaps unobstructed.

**RS‑485** polarity/termination verified; DI wiring and logic mode match configuration.

**Cut Mode** and **Lower/Upper** thresholds set per lamp/driver datasheet; start with light loads.

Upstream **MCB/RCD** sized for the load; enclosure closed before applying mains.

---

<a id="4-installation-quick-start"></a>

# System Architecture & Pinout

<div align="center">

| System Block Diagram | MCU Pinout |
| --- | --- |

| Field Board Layout | MCU Board Layout |
| --- | --- |

</div>

---

# ESPHome YAML Configuration & Hardware Pinout Manual

<div align="center">

| System Block Diagram | MCU Pinout |
| --- | --- |

| Field Board Layout | MCU Board Layout |
| --- | --- |

</div>

---

# Links

**Arduino / PlatformIO**

**C++** (direct RP2040 SDK)

*(MicroPython partially supported, but not recommended for precise dimming)*

---