Datasheet

DIO-430-R1 — Module for Smart I/O Control

Part No. TBD

# Product Description

The DIO-430-R1 is a configurable smart digital I/O module designed for digital input monitoring and relay-based output control in building automation, lighting, HVAC, alarms, and general control systems. It offers 4 opto-isolated digital inputs, 3 high-current SPDT relays, 3 user buttons, and 3 configurable user LEDs. All I/O channels are individually configurable, allowing flexible logic such as toggle, pulse, manual override, and alarm indication.

# Technical Specifications

| Specification | Details |
| --- | --- |
| Digital Inputs | 4; Opto-isolated, dry contact compatible, noise-protected |
| Relays | 3; SPDT (NO/NC), 16 A rated, dry contacts |
| LEDs | 3; Configurable: Steady or Blink modes, linked to relays |
| Buttons | 3; User-configurable for override or reset |
| Modbus RTU | Yes; RS-485 interface (Configurable: Addr 1–255, 9600–115200 baud) |
| USB-C | Yes; WebConfig tool access via Web Serial (Chrome/Edge) |
| Power | 24 V DC; Fused input, reverse-polarity and surge protected |
| MCU | RP2350; Dual-core, with QSPI flash, USB, UART, LittleFS |
| Protection | TVS, PTC; ESD, surge, and short-circuit protection on I/O and power |
| Relay Outputs | 3; SPDT (NO/NC/COM), 16 A dry contacts. Use RC/MOV snubbers or interposing contactors for inductive/mains loads. |
| User LEDs | 3; Configurable (Steady/Blink). Follow relay or logic status. |
| RS-485 (Modbus RTU) | 1; A/B/COM terminals. Daisy-chain topology. 120 Ω termination at both ends. |
| Power Input | 1; 24 V DC SELV. Reverse-polarity + surge protected. |
| Supply Voltage | 22 / 24 / 28 / V DC |
| Logic Consumption | – / 1.5 / 3.0 / W |
| Digital Input Range | 0 / 24 / 30 / V DC |
| Relay Contact Current | – / – / 16 / A |
| Relay Contact Voltage | – / – / 250 / V AC |
| RS-485 Data Rate | – / 19.2 / 115.2 / kbps |
| USB-C Voltage | 4.75 / 5.0 / 5.25 / V DC |
| Operating Temp. | 0 / – / 40 / °C |
| Mounting | DIN-rail EN 50022 (35 mm) |
| Enclosure | PC/ABS V-0, panel mount |
| Dimensions | 70 × 90.6 × 67.3 mm (W × H × D) |
| Terminals | Pluggable 5.08 mm, 26–12 AWG (≤ 2.5 mm²), 0.5–0.6 Nm |
| Ingress Protection | IP20 (panel interior) |
| Operating Temp | 0–40 °C, ≤ 95 % RH (non-condensing) |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type / pitch | Terminals ¦ Pluggable 5.08 mm, 26–12 AWG (≤ 2.5 mm²), 0.5–0.6 Nm ¦ |
| Environmental Ratings | Operating temperature | Operating Temp |
| Environmental Ratings | Ingress protection | Ingress Protection |
| Environmental Ratings | Relative humidity | 95 % RH |
| Mechanical & Packaging | Product dimensions | 70 × 90.6 × 67.3 mm |
| Mechanical & Packaging | Mounting | EN 50022 |
| Mechanical & Packaging | Net weight | 3 G |

# Compliance & Certifications

ce

ee

ce

ce

CE

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

RoHS

REACH

compliant components |

ee

ce

ce

ee

ee

ce

ee

ce

ce

ee

ce

ee

ee

ce

ce

ce

ee

ee

ce

ee

ce

ce

ce

ce

ce

ee

ce

ee

ce

ee

ce

ce

ce

ce

ee

ce

ee

ee

ce

ce

ce

ce

ee

ce

ee

ee

ce

ee

ce

ce

ce

ee

ee

ce

ee

ce

ce

ee

ce

ee

ce

ee

ee

ee

ce

ce

ee

ce

ce

ce

ce

ee

ce

ce

ee

ce

ee

ce

ce

ce

ee

ee

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

CE

ee

CE

ce

ee

ee

ee

ee

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu