# DIO-430-R1 — Module for Smart I/O Control

DIN rail • 24 V DC • Modbus RTU • Home Assistant

# Overview

The **DIO-430-R1** is a configurable smart digital I/O module designed for **digital input monitoring and relay-based output control** in **building automation, lighting, HVAC, alarms, and general control systems**.

It offers **4 opto-isolated digital inputs**, **3 high-current SPDT relays**, **3 user buttons**, and **3 configurable user LEDs**. All I/O channels are individually configurable, allowing flexible logic such as toggle, pulse, manual override, and alarm indication.

It connects via **RS-485 (Modbus RTU)** to a **MicroPLC, MiniPLC, or any compatible controller**, and can also integrate with **Home Assistant (ESPHome)** or **SCADA/PLC systems**.

Configuration and diagnostics are performed through a driverless **Web Serial interface via USB-C**, using the browser-based **WebConfig Tool**. The module supports both **master-controlled** and **standalone local logic** modes.

| Subsystem | Qty | Description |
| --- | --- | --- |
| Digital Inputs | 4 | Opto-isolated, dry contact compatible, noise-protected |
| Relays | 3 | SPDT (NO/NC), 16 A rated, dry contacts |
| LEDs | 3 | Configurable: Steady or Blink modes, linked to relays |
| Buttons | 3 | User-configurable for override or reset |
| Modbus RTU | Yes | RS-485 interface (Configurable: Addr 1–255, 9600–115200 baud) |
| USB-C | Yes | WebConfig tool access via Web Serial (Chrome/Edge) |
| Power | 24 V DC | Fused input, reverse-polarity and surge protected |
| MCU | RP2350 | Dual-core, with QSPI flash, USB, UART, LittleFS |
| Protection | TVS, PTC | ESD, surge, and short-circuit protection on I/O and power |

## System Role & Communication

The module communicates over the **RS-485 Modbus RTU bus**, using A/B differential lines and a shared COM/GND reference. It supports **poll-based communication**, where a master device reads input states and writes relay commands.

All configuration — including input-to-relay mapping, LED modes, and button logic — is stored persistently in internal flash via **LittleFS** and can be changed live through **USB-C + WebConfig**.

**Factory default communication settings:**

**Modbus Address:** `3`

**Baud Rate:** `19200`

**Parity:** `None`

**Stop Bits:** `1`

The module’s logic (input→relay mapping, LED modes, button behavior) is stored persistently in internal flash via **LittleFS**, and settings can be changed live using **USB-C + WebConfig**.

---

# Quick Overview

See module README for details.

# Typical Applications

The **DIO‑430‑R1** supports both **lighting** and **motor/pump control** — making it ideal for mixed automation tasks in smart homes, greenhouses, HVAC, and industrial setups.

Below are 3 versatile examples combining both types of loads.

---

# Tech Specs

See module README for details.

# Installation, Environmental & Mechanical

| Property | Specification |
| --- | --- |
| Mounting | DIN-rail EN 50022 (35 mm) |
| Enclosure | PC/ABS V-0, panel mount |
| Dimensions | 70 × 90.6 × 67.3 mm (W × H × D) |
| Terminals | Pluggable 5.08 mm, 26–12 AWG (≤ 2.5 mm²), 0.5–0.6 Nm |
| Ingress Protection | IP20 (panel interior) |
| Operating Temp | 0–40 °C, ≤ 95 % RH (non-condensing) |

---

# Home Assistant & ESPHome Integration

The DIO-430-R1 joins your system over **RS-485 (Modbus RTU)**. Setup has two parts:

1) **Physical wiring**, 2) **Digital configuration** (WebConfig → optional PLC/ESPHome).

---

# Documentation

**Firmware binaries**

Default UF2: `DIO-430-R1/Firmware/default_DIO_430_R1/build/rp2040.rp2040.generic_rp2350/`

**YAML configs (ESPHome)**

Package & examples: `DIO-430-R1/Firmware/default_dio_430_r1_plc/`

**WebConfig tool (HTML/JS)**

`DIO-430-R1/Firmware/ConfigToolPage.html`

**Schematics (PDF)**

Field Board: `Schematics/DIO-430-R1-FieldBoard.pdf`

MCU Board: `Schematics/DIO-430-R1-MCUBoard.pdf`

**Images & diagrams**

`DIO-430-R1/Images/`

**Datasheets**

Refer to the `Schematics/` folder BOM notes for part numbers (e.g., ISO1212, MAX485, HF115F).

---

# Power Supply

[ ] All wiring is torqued, labeled, and strain-relieved

[ ] **No bridge** between logic **GND** and isolated **GND_ISO/FGND**

[ ] Panel PE is bonded; SELV supply negative and COM/GND are properly landed

[ ] RS-485 **A/B** polarity and **120 Ω** termination confirmed at bus ends

[ ] Relay loads do **not** exceed the contact rating; snubbers added for inductive loads

[ ] Inputs wired to **dry contact/SELV** only; sensor polarity and returns verified

[ ] USB-C used only for configuration; disconnected for normal operation

---

# Inputs & Outputs

| Interface | Qty | Description |
| --- | --- | --- |
| **Digital Inputs** | 4 | Galvanically isolated (ISO1212 class). Supports dry contacts or 24 V signals. PTC + TVS per channel. |
| **Relay Outputs** | 3 | SPDT (NO/NC/COM), 16 A dry contacts. Use RC/MOV snubbers or interposing contactors for inductive/mains loads. |
| **User LEDs** | 3 | Configurable (Steady/Blink). Follow relay or logic status. |
| **Buttons** | 3 | Momentary. Configurable for relay override/toggle. |
| **RS-485 (Modbus RTU)** | 1 | A/B/COM terminals. Daisy-chain topology. 120 Ω termination at both ends. |
| **USB-C** | 1 | Web Serial setup, diagnostics, and firmware flashing (ESD-protected). |
| **Power Input** | 1 | 24 V DC SELV. Reverse-polarity + surge protected. |

**Electrical Ratings**

| Parameter | Min | Typ | Max | Unit | Notes |
| --- | --- | --- | --- | --- | --- |
| Supply Voltage | 22 | 24 | 28 | V DC | SELV/PELV input |
| Logic Consumption | – | 1.5 | 3.0 | W | Excludes relay loads |
| Digital Input Range | 0 | 24 | 30 | V DC | Isolated, noise-protected |
| Relay Contact Current | – | – | 16 | A | SPDT dry contacts |
| Relay Contact Voltage | – | – | 250 | V AC | or 30 V DC max |
| RS-485 Data Rate | – | 19.2 | 115.2 | kbps | Default 19200 8N1 |
| USB-C Voltage | 4.75 | 5.0 | 5.25 | V DC | Service only |
| Operating Temp. | 0 | – | 40 | °C | ≤ 95 % RH, non-condensing |

**Power budgeting:** logic + LEDs + up to 3 relay coils + sensor loads → add ≥ 30 % PSU headroom.

---

# Cable Recommendations & Shield Grounding

## 🔌 Power

| Area | Warning |
| --- | --- |
| 24 V DC Input | Use a clean, fused SELV supply. Reverse-polarity protection exists but may disable the module when triggered. |
| Sensor Rail | Power sensors from a SELV rail. Observe polarity. Fuse external branches as required. |
| Surge/Noise | In noisy panels, add upstream surge/EMI suppression and keep high-current wiring away from control wiring. |

## ⏽ Inputs (Digital)

| Area | Warning |
| --- | --- |
| Type | **Dry contact / 24 V signaling only**, per your standard. Do not inject mains or undefined levels. |
| Isolation | Inputs are isolated from logic. Keep sensor returns on the **field/isolated** domain; do not bond to logic GND. |
| Debounce | Firmware provides debounce, but route away from contactors/VFDs and use shielded/twisted pairs for long runs. |
| Polarity | Configure invert/action in WebConfig; verify state transitions after wiring. |

## ⚙️ Relays (Outputs)

| Area | Warning |
| --- | --- |
| Contact Type | **SPDT (NO/NC/COM)** dry contacts. Follow the contact rating on the device label/datasheet. |
| Inductive Loads | For motors/solenoids/contactors, add an **RC snubber or MOV** at the load. Consider interposing relays/ contactors for higher power. |
| Separation | Keep relay load wiring physically separate from signal wiring. De-energize before servicing. |
| Verification | After wiring, verify NO/NC behavior and load polarity before enabling automation. |

## 🖧 RS-485 (Modbus RTU)

| Area | Warning |
| --- | --- |
| Topology | Use twisted pair; **daisy-chain** (no stubs). Terminate with **120 Ω** at both physical ends. |
| Polarity | Maintain **A/B** polarity consistently. Share **COM/GND** reference between nodes (same SELV domain). |
| EMC | Route away from VFDs, contactors, and mains bundles. Use shielded cable in high-EMI environments. |
| Protection | Port includes protection, but good wiring practice is still required to avoid transients. |

## 🔌 USB-C (Front / Setup)

| Area | Warning |
| --- | --- |
| Purpose | **Setup & maintenance only** (WebConfig / firmware). Not intended for powering field devices. |
| ESD/EMI | Avoid hot-plugging in high-EMI areas. Use a grounded service laptop. Disconnect after commissioning. |

## 🔆 Front Panel (Buttons & LEDs)

| Area | Warning |
| --- | --- |
| Buttons & LEDs | Buttons can override relays; document operating procedures. Lock out overrides for safety-critical installs. |

## 🛡️ Shielding & EMC

| Area | Recommendation |
| --- | --- |
| Cable Shields | Terminate shields at **one end** (typically the PLC/controller). Keep runs short and away from high-voltage/EMI sources. |

---

# System Architecture & Pinout

System overview, board callouts, and pin mapping:

---

# ESPHome YAML Configuration & Hardware Pinout Manual

System overview, board callouts, and pin mapping:

---

# Links

**Arduino**

**C++** (PlatformIO)

**MicroPython** (community builds for RP23xx-class MCUs)

---