# ENM-223-R1 — 3-Phase Power Metering & I/O Module

DIN rail • 24 V DC • Modbus RTU • Home Assistant

# Overview

See module README for details.

# Quick Overview

The **ENM‑223‑R1** is a modular **3‑phase energy metering + I/O** device for power monitoring, automation, and local control. It features **3 voltage channels (L1/L2/L3‑N)**, **3 current channels (external CTs)**, **2 SPDT relays**, **4 user LEDs**, and **4 buttons**—all driven by an **RP2350** MCU with QSPI flash and a dedicated **ATM90E32AS** metering IC.

It integrates with **MiniPLC/MicroPLC** controllers or any **Modbus RTU** master over **RS‑485**, and it’s configured in‑browser via **USB‑C Web Serial** (no drivers). Typical uses include **energy dashboards, demand response, alarm‑driven relay control, and building automation**. Defaults ship as **Modbus address 3 @ 19200 8N1** (changeable in WebConfig).

Quick device flow:

**Wire Lx/N/PE + CTs → set address/baud in WebConfig → calibrate gains/offsets → define alarms per L1/L2/L3/Totals → map relays/LEDs/buttons → connect RS‑485 A/B (and GND if separate PSUs) → poll via Modbus.**

---

# Typical Applications

This section outlines practical application examples for the **ENM‑223‑R1** module. Each use case includes a functional goal and a clear configuration procedure using the WebConfig tool and/or Modbus RTU integration.

These templates are applicable in energy management, automation, industrial control, and building infrastructure deployments.

---

# Tech Specs

---

# Installation, Environmental & Mechanical

<div align="center">

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/photo1.png" width="320"><br>

</div>

| Property | Specification |
| --- | --- |
| **Mounting** | DIN rail EN 50022 (35 mm) |
| **Material / Finish** | PC / ABS V-0, matte light gray + smoke panel |
| **Dimensions (L × W × H)** | 70 × 90.6 × 67.3 mm (9 division units) |
| **Weight** | ~420 g |
| **Terminals** | 300 V / 20 A / 26–12 AWG (2.5 mm²) / torque 0.5–0.6 Nm / pitch 5.08 mm |
| **Ingress Protection** | IP20 (EN 60529) |
| **Operating Temp.** | 0–40 °C / ≤95 % RH (non-condensing) |

<div align="center">

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/ENMDimensions.png" alt="Mechanical Dimensions" width="420"><br>

<em>ENM-223-R1 Physical Dimensions (DIN-rail enclosure)</em>

</div>

---

# Home Assistant & ESPHome Integration

The **ENM‑223‑R1** connects to your system over **RS‑485 (Modbus RTU)** and supports configuration via **USB‑C WebConfig**. Setup involves:

**1) Physical wiring**, **2) Digital setup** (WebConfig → Modbus or PLC/ESPHome control).

---

# Documentation

The following key project resources are included in this repository:

🧠 **Firmware (Arduino/PlatformIO)**

`firmware/default_enm_223_r1.ino`

Core firmware implementing Modbus RTU, alarm logic, relays, LED control, overrides, and WebConfig support.

🧰 **WebConfig Tool**

`tools/ConfigToolPage.html`

HTML-based USB Web Serial interface for live configuration, calibration, alarm setup, and logic assignment.

🖼 **Images & UI Diagrams**

`Images/`

Contains front-panel photos, system diagrams, wiring illustrations, and screenshots from WebConfig UI.

📐 **Hardware Schematics**

`Schematics/`

Includes PDF schematics for Field Board and MCU Board — ideal for developers, reviewers, or third-party modders.

📄 **Datasheets & Manuals**

`ENM-223-R1 Datasheet.pdf`

Covers full electrical and mechanical specs, terminal layout, block diagram, and pinout.

📦 **ESPHome YAML Templates**

`ENM223R1_ESPHome_Integration_Guide.md`

Ready-to-use `packages:` block for ESPHome controllers, with sensors, relays, alarms, override logic, and Home Assistant tips.

🔁 Latest releases can also be found in the Releases tab or in the `Firmware/` directory.

---

# Power Supply

**HOMEMASTER – Modular control. Custom logic.**

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/photo1.png" align="right" width="440" alt="MODULE photo">

## Module Description

The **ENM-223-R1** is a configurable smart I/O module designed for **3-phase power quality and energy metering**.

It includes **3 voltage inputs, 3 current channels**, **2 relays**, and optional **4 buttons / 4 LEDs**, with configuration via **WebConfig** using **USB-C (Web Serial)**.

It connects over **RS-485 (Modbus RTU)** to a **MicroPLC/MiniPLC**, enabling use in **energy monitoring, automation, and smart building applications**.

---

# Inputs & Outputs

| Interface | Qty | Description |
| --- | --- | --- |
| **Voltage Inputs** | 3 | L1 / L2 / L3–N, 85–265 V AC via precision divider to ATM90E32AS metering IC |
| **Current Inputs** | 3 | CT1–CT3, external 333 mV / 1 V RMS split-core CTs |
| **Relay Outputs** | 2 | SPDT dry contact, HF115F series, opto-driven; 5 A @ 250 VAC / 30 VDC (module limit) |
| **User LEDs** | 4 | Assignable status / override indicators (GPIO18–21) |
| **Buttons** | 4 | Momentary tactile switches (GPIO22–25) |
| **RS-485** | 1 | A/B/COM, Modbus RTU, MAX485 transceiver |
| **USB-C** | 1 | Native USB 2.0 (Web Serial + firmware flashing), ESD-protected |
| **Power Input** | 1 | 24 V DC (22–28 V) logic supply, reverse & surge protected |

---

# Cable Recommendations & Shield Grounding

## ⚡ Power

| Area | Warning |
| --- | --- |
| **24 V DC Input** | Use a clean, fused SELV power source. Reverse polarity is protected but may disable the module. |
| **Voltage Input** | Connect **L1/L2/L3/N/PE** only within rated range (85–265 V AC). Use circuit protection upstream. |
| **Sensor Domain** | Use **CTs with 1 V or 333 mV RMS** output. Never apply 5 A directly. Observe polarity and shielding. |

## 🧲 Inputs & Relays

| Area | Warning |
| --- | --- |
| **CT Inputs** | Accept only voltage-output CTs. Reversing polarity may affect power sign. Use GND_ISO reference. |
| **Relay Outputs** | Dry contacts only. Rated: **5 A @ 250 VAC or 30 VDC**. Use snubber (RC/TVS) for inductive loads. |

## 🖧 Communication & USB

| Area | Warning |
| --- | --- |
| **RS‑485 Bus** | Use **twisted pair**. Terminate at both ends. Match A/B polarity. Share GND if powered from different PSUs. |
| **USB-C (Front)** | For **setup only**. Not for permanent field connection. Disconnect during storms or long idle periods. |

## 🎛 Front Panel

| Area | Warning |
| --- | --- |
| **Buttons & LEDs** | Can override relays or trigger alarms. Use firmware settings or lockout for safety-critical installs. |

## 🛡 Shielding & EMC

| Area | Recommendation |
| --- | --- |
| **Cable Shields** | Terminate at one side only (preferably PLC/controller). Route away from VFDs and high-voltage cabling. |

---

## ✅ Pre‑Power Checklist

[x] All wiring is torqued, labeled, and strain-relieved

[x] **No bridge between logic GND and GND_ISO**

[x] PE and N are wired to terminals

[x] RS‑485 A/B polarity and 120 Ω termination confirmed

[x] Relay loads do **not** exceed 5 A or contact voltage rating

[x] CTs installed with correct polarity and securely landed

[x] Voltage inputs fused, protected, and within spec (85–265 V AC)

🧷 **Tip:** In single-phase installations, energize **L1** and tie **L2/L3 → N** to prevent phantom voltages.

<a id="4-installation-quick-start"></a>

# System Architecture & Pinout

<div align="center">

<table>

<tr>

<td align="center">

<strong>System Diagram</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/ENM_Diagram.png" alt="System Block Diagram" width="340">

</td>

<td align="center">

<strong>MCU Pinout</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/ENM_MCU_Pinouts.png" alt="RP2350 MCU Pinout" width="340">

</td>

</tr>

<tr>

<td align="center">

<strong>Field Board Terminal Map</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/FieldBoard_Diagram.png" alt="Field Board Layout" width="340">

</td>

<td align="center">

<strong>MCU Board Layout</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/MCUBoard_Diagram.png" alt="MCU Board Layout" width="340">

</td>

</tr>

</table>

</div>

💡 **Note:** Pinouts correspond to hardware revision R1. Terminals are pluggable 5.08 mm pitch (26–12 AWG, torque 0.5–0.6 Nm).

---

# ESPHome YAML Configuration & Hardware Pinout Manual

<div align="center">

<table>

<tr>

<td align="center">

<strong>System Diagram</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/ENM_Diagram.png" alt="System Block Diagram" width="340">

</td>

<td align="center">

<strong>MCU Pinout</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/ENM_MCU_Pinouts.png" alt="RP2350 MCU Pinout" width="340">

</td>

</tr>

<tr>

<td align="center">

<strong>Field Board Terminal Map</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/FieldBoard_Diagram.png" alt="Field Board Layout" width="340">

</td>

<td align="center">

<strong>MCU Board Layout</strong><br>

<img src="https://raw.githubusercontent.com/isystemsautomation/HOMEMASTER/main/ENM-223-R1/Images/MCUBoard_Diagram.png" alt="MCU Board Layout" width="340">

</td>

</tr>

</table>

</div>

💡 **Note:** Pinouts correspond to hardware revision R1. Terminals are pluggable 5.08 mm pitch (26–12 AWG, torque 0.5–0.6 Nm).

---

# Links

**MicroPython**

**C/C++**

**Arduino IDE**

---