Datasheet

ENM-223-R1 — 3-Phase Power Metering & I/O Module

Part No. TBD

# Product Description

The ENM-223-R1 is a configurable smart I/O module designed for 3-phase power quality and energy metering. It includes 3 voltage inputs, 3 current channels, 2 relays, and optional 4 buttons / 4 LEDs, with configuration via WebConfig using USB-C (Web Serial).

# Technical Specifications

| Specification | Details |
| --- | --- |
| Voltage Inputs | 3; L1/L2/L3‑N measurement (divider network on FieldBoard) feeding ATM90E32AS |
| Current Inputs | 3; Differential CT inputs (IAP/IAN, IBP/IBN, ICP/ICN) with filtering/burdens |
| Relays | 2; SPDT dry contacts (NO/NC); opto‑driven; alarm‑ or Modbus‑controlled |
| LEDs | 4; User LEDs; sources: overrides/alarms/warnings/events; steady or blink |
| Buttons | 4; User actions (toggle relays/LEDs, overrides, acks) with live state feedback |
| Metering & Energy | —; ATM90E32AS: Urms/Irms, P/Q/S, PF, angle, freq; energy kWh/kvarh/kVAh (phase & totals) |
| Config UI | Web Serial; In‑browser WebConfig over USB‑C (Chrome/Edge); live meter, calibration, alarms, relays, LEDs, buttons |
| Modbus RTU | RS‑485; Multi‑drop slave; address 1…255; baud 9600–115200 (default 19200 8N1) |
| MCU | RP2350 + QSPI; Dual‑core MCU, native USB, external W25Q32 flash; RS‑485 via MAX485 transceiver |
| Power | 24 VDC; Buck to 5 V → 3.3 V LDO; isolated analog domain via B0505S DC‑DC + ISO7761 |
| Protection | TVS, PTC, fuses; Surge/ESD on USB & RS‑485; resettable fuses on field I/O; reverse‑polarity protection |
| Relay Outputs | 2; SPDT dry contact, HF115F series, opto-driven; 5 A @ 250 VAC / 30 VDC (module limit) |
| User LEDs | 4; Assignable status / override indicators (GPIO18–21) |
| RS-485 | 1; A/B/COM, Modbus RTU, MAX485 transceiver |
| USB-C | 1; Native USB 2.0 (Web Serial + firmware flashing), ESD-protected |
| Power Input | 1; 24 V DC (22–28 V) logic supply, reverse & surge protected |
| Supply Voltage (V+) | 22 / 24 / 28 / V DC |
| Power Consumption | – / 1.85 / 3.0 / W |
| Logic Rails | – / 3.3 / 5 / – / V |
| Isolated Sensor Rails | – / +12 / +5 / – / V |
| RS-485 Bus | – / 115.2 / – / kbps |
| USB-C Port | – / 5 / 5.25 / V DC |
| Operating Temp. | 0 / – / 40 / °C |
| Isolation (DC-DC) | – / 1.5 / 3.0 / kV DC |
| Isolation (Digital) | – / 5.0 / – / kV RMS |
| Mounting | DIN rail EN 50022 (35 mm) |
| Material / Finish | PC / ABS V-0, matte light gray + smoke panel |
| Dimensions (L × W × H) | 70 × 90.6 × 67.3 mm (9 division units) |
| Weight | ~420 g |
| Terminals | 300 V / 20 A / 26–12 AWG (2.5 mm²) / torque 0.5–0.6 Nm / pitch 5.08 mm |
| Ingress Protection | IP20 (EN 60529) |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type / pitch | Terminals are pluggable 5.08 mm pitch (26–12 AWG, torque 0.5–0.6 Nm). |
| Environmental Ratings | Operating temperature | Operating Temp |
| Environmental Ratings | Ingress protection | Ingress Protection |
| Environmental Ratings | Relative humidity | 95 % RH |
| Mechanical & Packaging | Product dimensions | 70 × 90.6 × 67.3 mm |
| Mechanical & Packaging | Mounting | DIN Rail |
| Mechanical & Packaging | Net weight | 1 G |

# Compliance & Certifications

ce

ee

ce

ce

CE

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ee

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ee

ce

ee

ee

ce

ce

ce

ce

ee

ee

ee

ee

ce

ce

ce

ce

ce

ce

ce

ee

ee

ce

ce

ce

ee

ee

ce

ce

ce

RoHS

REACH

compliant |

ce

ce

ee

EE

ce

ee

ce

ee

ee

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

CE

ce

ce

ee

ee

ee

ee

ee

ce

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu