Datasheet

RGB-621-R1 — Module for RGB+CCT LED Control

Part No. TBD

# Product Description

# 🚧 Project Status: Under Active Development & Testing

# Technical Specifications

| Specification | Details |
| --- | --- |
| Digital Inputs | 2; Galvanically isolated (ISO1212) dry-contact inputs with surge and reverse protection |
| PWM Outputs | 5; N-channel MOSFET drivers (AP9990GH-HF), 12 V / 24 V LED channels for R / G / B / CW / WW |
| Relay Output | 1; SPST-NO relay (HF115F/005-1ZS3), 5 V coil, rated 16 A @ 250 VAC / 30 VDC |
| Buttons | 2; Local control or configuration triggers (SW1 / SW2) |
| LED Indicators | 8; Power, TX/RX, input, and status LEDs for feedback and diagnostics |
| Modbus RTU | Yes; RS-485 interface via MAX485CSA+T transceiver; 120 Ω termination selectable |
| USB-C | Yes; WebConfig & firmware flashing with PRTR5V0U2X ESD protection |
| Power Input | 24 V DC; Protected by resettable fuses (1206L series), TVS (SMBJ33A), and reverse-blocking (STPS340U) |
| Logic Supply | —; AP64501SP-13 buck (5 V) + AMS1117-3.3 LDO chain |
| MCU | RP2350A; Dual-core Arm Cortex-M33 @ 133 MHz with 32 Mbit QSPI Flash (W25Q32JVUUIQ) |
| Isolation & Protection | —; Galvanic isolation, TVS diodes, PTC fuses, transient suppression on all field I/O |
| Relay | 1; SPST-NO, 16 A @ 250 VAC / 30 VDC |
| RS-485 (Modbus) | 1; MAX485 transceiver, 19200 bps 8N1 default |
| Buttons / LEDs | —; Local control, TX/RX & status indicators |
| Supply Voltage | 20 V / 24 V / 30 V / SELV input protected |
| Power Use | — / 1.85 W / 3.0 W / No LED load |
| Relay Contacts | — / — / 16 A @ 250 VAC / 30 V DC / Resistive |
| PWM Current | — / — / 5 A per ch / External PSU limited |
| RS-485 Rate | — / — / 115.2 kbps / Half-duplex |
| USB Voltage | 4.75 V / 5 V / 5.25 V / Logic only |
| Operating Temp | 0 °C / — / 40 °C / ≤ 95 % RH |
| Nominal Voltage | 24 V DC ± 10 % |
| Input Protection | PTC fuses (F1–F4), reverse-polarity diode (STPS340U), surge TVS (SMBJ33A) |
| Ground Reference | Field return `GND_FUSED` |
| Isolation | Field side isolated from logic via DC/DC and opto-devices |
| Notes | Use a regulated SELV 24 V DC supply rated ≥ 1 A per module. Each module must have its own isolated 24 V supply rail. |
| Type | Galvanically isolated, dry-contact or sourcing 24 V DC input |
| Circuit | ISO1212 receiver with TVS (SMBJ26CA) + PTC protection |
| Operating Range | 9 – 36 V DC (typ. 24 V DC) |
| Coil Voltage | 5 V DC (via SFH6156 optocoupler + S8050 driver) |
| Contact Rating | 16 A @ 250 VAC / 30 V DC (resistive) |
| Protection | External RC snubber / flyback diode recommended |
| Transceiver | MAX485CSA+T |
| Bus Type | Differential, multi-drop (A/B lines) |
| Default Settings | 19200 bps · 8N1 |
| Termination | 120 Ω enabled only at end-of-line device |
| Function | WebConfig setup & firmware update only |
| Supply | 5 V DC from host computer (logic domain) |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type | Not specified in README |
| Environmental Ratings | Operating temperature | Operating Temp |
| Environmental Ratings | Ingress protection | IP20 |
| Environmental Ratings | Relative humidity | 95 % RH |
| Mechanical & Packaging | Product dimensions | 52.5 × 90.6 × 67.3 mm |
| Mechanical & Packaging | Mounting | EN 50022 |
| Mechanical & Packaging | Net weight | 9990G |

# Compliance & Certifications

ce

ee

ce

ce

CE

ee

ce

CSA+T transceiver; 120 Ω terminat

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ee

ce

ce

ce

ce

ce

ce

ee

ce

ee

ee

ce

ce

ce

ce

ce

ee

ce

CSA+T |

ce

ce

ee

ee

ce

ce

ce

ce

ee

ce

ce

ce

ee

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

CE

ee

ee

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu