Datasheet

STR-3221-R1 — Module for Smart Lighting & I/O Control

Part No. TBD

# Product Description

# STR-3221-R1 — Module for Smart Lighting & I/O Control

# Technical Specifications

| Specification | Details |
| --- | --- |
| Digital Inputs | 3; Opto-isolated 3V3 DC on terminals: IN1 (GND,+), IN2 (GND,+) for motion sensors, One DI for switch |
| MOSFET Outputs | 32; Low-side SI2307A per channel (O1…O32), 12–24 V loads; flyback SS24 diodes; grouped with shared VCC pins. |
| LED Driver ICs | 4; TLC59208F (8-ch constant-current sinks) used for status/indication and channel grouping/PWM. |
| Buttons | 4; SW1–SW4 for test/override or user logic. |
| Status LEDs | 4; User-assignable (steady/blink) for power/activity/logic states. |
| Modbus RTU | Yes; RS-485 via MAX485 transceiver; activity LEDs. |
| USB-C | Yes; WebConfig over Web Serial (Chromium-based browsers); ESD-protected port. |
| Power | 24 VDC; Reverse/surge-protected input; AP64501 buck → 5 V, AMS1117-3.3 LDO → 3.3 V logic. |
| MCU | RP2350 + W25Q32; Dual-core MCU with external QSPI flash for firmware/config. |
| Protection | TVS, PTC; Surge/ESD and resettable fuses across field & comms lines. |
| Outputs | 32; Low-side MOSFET (SI2307A) channels with SS24 flyback diodes, grouped with shared VCC rails. |
| RS-485 (Modbus RTU) | 1; Communication bus; A/B/COM terminals. |
| USB-C (Setup Port) | 1; WebConfig / firmware interface (not for powering field devices). |
| Power Input | 1; 24 VDC (V+, 0V); reverse and surge-protected; onboard 5 V / 3.3 V regulation. |
| Sensor Rails (SENS.A / SENS.B) | 2 pairs; Fused 24 V auxiliary rails for external sensors (low current). |
| Supply Voltage (V+) | 20 / 24 / 30 / VDC |
| Logic Rails | — / 5 / 3.3 / — / VDC |
| Quiescent Current (no load) | — / 60 / 100 / mA |
| Full-Load Current (all outputs) | — / — / 3.0 / A |
| Digital Input Range | 9 / 24 / 30 / VDC |
| Input Threshold (ON) | — / 8 / — / VDC |
| Sensor Rail Output | — / 24 / — / VDC |
| Output Type | — / — / — / — |
| Flyback Protection | — / — / — / — |
| Communication | — / — / — / — |
| Isolation | — / — / — / — |
| Operating Temperature | 0 / — / 40 / °C |
| Board | Generic RP2350 |
| Flash Size | 2 MB (Sketch 1 MB / FS 1 MB) |
| Upload Port | USB-C |
| Baud Rate | 115200 |
| Libraries | Modbus RTU, SimpleWebSerial, JSON, LittleFS, Wire |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type | Not specified in README |
| Environmental Ratings | Operating temperature | Operating Temp |
| Environmental Ratings | Ingress protection | Not specified in README |
| Environmental Ratings | Relative humidity | 95 % RH |
| Mechanical & Packaging | Product dimensions | Not specified in README |
| Mechanical & Packaging | Mounting | 35 mm DIN |
| Mechanical & Packaging | Net weight | 1 G |

# Compliance & Certifications

ee

ce

ce

CE

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ee

ce

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

CE

ce

ce

ce

ce

ee

ee

ee

ce

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu