# 1. Introduction

DIN rail • 24 V DC • Modbus RTU • Home Assistant

# Overview

See module README for details.

# Quick Overview

The **WLD-521-R1** is a DIN‑rail smart I/O module for **leak detection**, **pulse water metering**, **ΔT heat monitoring**, and **local irrigation control**. It exposes **5 opto‑isolated digital inputs**, **2 SPDT relays**, **4 user buttons**, and **4 status LEDs** and is serviced over **USB‑C**.

It integrates with a **MiniPLC/MicroPLC** (or other PLC/SCADA/HA controllers) via **Modbus RTU over RS‑485**. Configuration is done in a browser using the **WebConfig** tool (Web Serial over USB‑C): set Modbus params, choose per‑input modes (sensor/counter), link 1‑Wire temperature sensors, and enable autonomous irrigation/flow‑safety logic.

**In one line:** a resilient water‑safety/flow module with local logic that still plays perfectly with your PLC and Home Assistant stack.

---

# Typical Applications

The **WLD-521-R1** supports a range of real-world applications in leak detection, flow metering, hydronic energy monitoring, and irrigation control. Below are practical scenarios with step-by-step configuration.

---

## 💧 1) Basement Leak Alarm + Auto Shut-off

**Goal:** Detect water leaks and immediately shut off the water supply using a relay-controlled valve.

**Steps:**

Set **DI1** as **Water sensor**

Enable DI1 and set **Action = Toggle**

Set **Control target = Relay 1**

Wire a **motorized shut-off valve** (normally open) to **R1**

(Optional) Assign **LED1** to blink on **DI1** or **R1**

---

## 🌿 2) Garden Irrigation with Flow Supervision

**Goal:** Automate watering safely with flow monitoring and environmental interlocks.

**Steps:**

Go to **Irrigation → Zone 1**

Set **Valve relay = Relay 2**, **Flow DI = DI2**

Enable **Use flow supervision**

Configure:

**Min rate = 0.2 L/min**

**Grace = 8 s**

**Timeout = 1200 s**

**Target liters = 50**

Add interlocks:

**DI_moist = DI3** (dry = run)

**DI_rain = DI4** (rain = block)

**R_pump = Relay 1** (pump ON when watering)

Enable **Window: 06:00–08:00** with **Auto-start**

---

## 📈 3) Water Consumption Metering (Billing)

**Goal:** Track water usage in liters using pulse flow meters.

**Steps:**

Set **DI2** to **Water counter**

Enter **Pulses per liter = 450** (typical)

Adjust **Rate × / Total ×** as needed for calibration

Use **Reset total** to baseline reading

Use **Calc from external** after external validation

View **Live rate (L/min)** and **Total (L)** in WebConfig

---

## 🔥 4) Heat Energy Monitoring (Hydronic ΔT Loops)

**Goal:** Measure heat power and energy from flow and temperature sensors.

**Steps:**

Set **DI3 = Water counter**

Enable **Heat** on DI3

Assign **Sensor A = #1 (supply)**, **Sensor B = #2 (return)**

Set thermal constants:

**cp = 4186 J/kg·°C**

**ρ = 1.0 kg/L**

Adjust **Calibration ×** if needed

View **TA**, **TB**, **ΔT**, **Power (W)**, **Energy (J/kWh)**

Use **Reset energy** to zero counters

---

<a id="3-safety-information"></a>

# Tech Specs

This section consolidates diagrams, I/O, electrical limits, firmware behavior, connector map, mechanics, and compliance for quick reference.

---

# Installation, Environmental & Mechanical

**Mounting:** DIN rail EN 50022, 35 mm

**Enclosure:** PC/ABS, V‑0, light gray/black, matte

**Terminals:** 5.08 mm pitch; 26–12 AWG (to 2.5 mm²); **0.5–0.6 Nm** torque

---

# Home Assistant & ESPHome Integration

See module README for details.

# Documentation

**Firmware binaries** — `Firmware/default_wld_521_r1/`

**ESPHome YAML configs** — `Firmware/default_wld_521_r1_plc/`

**WebConfig Tool** — `Firmware/ConfigToolPage.html`

**Schematics** — `Schematics/WLD-521-R1-FieldBoard.pdf`, `Schematics/WLD-521-R1-MCUBoard.pdf`

**Images & diagrams** — `Images/`

**Datasheet** — `Manuals/WLD-521-R1 Datasheet.pdf`

---

<a id="12-support"></a>

# Power Supply

The WLD‑521‑R1 operates from a **regulated 24 VDC supply** connected to the top terminals labeled `V+` and `0V`. The power supply should be SELV-rated and appropriately sized.

## Power Supply Notes

Input: **24 VDC**, reverse-protected and fused onboard

Internal regulation:

**5 V logic** (buck regulated via AP64501)

**3.3 V logic** (via AMS1117-3.3)

**+12 V ISO** (for field sensors via B2412S‑2WR3)

**+5 V ISO** (via B2405S‑2WR3)

## Power Budget (Estimates)

| Load | Typical Current |
| --- | --- |
| Base logic + LEDs | ~50 mA |
| Each relay (coil) | ~40–60 mA |
| Sensor rails (total) | ≤150 mA (shared between +5 V ISO / +12 V ISO) |

**Recommended PSU:** ≥300 mA per module (with 30% headroom).

⚠️ Only use the **sensor rails** for **low-power sensors** like leak probes and flow meters.

Never power relays, valves, or actuators from the module’s +5 V / +12 V outputs.

---

# Inputs & Outputs

| Interface | Qty | Description |
| --- | --- | --- |
| **Digital Inputs** | 5 | Opto‑isolated DI (dry contact / open‑collector / pulse for flow meters); isolated return (GND_ISO). |
| **Relay Outputs** | 2 | SPDT dry contact (NO/C/NC); snubbered; local/Modbus/logic control. |
| **User LEDs** | 4 | Configurable (Solid/Blink) for DI/Relay/Irrigation/Override feedback. |
| **User Buttons** | 4 | Assignable actions (Relay toggle/pulse, Override, Irrigation start/stop). |
| **RS‑485 (Modbus)** | 1 | Half‑duplex multi‑drop; A/B/COM terminals; fail‑safe & surge‑protected. |
| **USB‑C** | 1 | Service/setup via WebConfig (Web Serial). |
| **1‑Wire Bus** | 1 | +5 V / DATA / GND (logic domain) for DS18B20 sensors. |
| **Sensor Power** | 2 | Isolated +12 V / +5 V rails for **low‑power sensors only** (fused, filtered). |

---

# Cable Recommendations & Shield Grounding

## 🔌 Power

| Interface | Warning |
| --- | --- |
| **V+ / 0V (Top-left)** | Connect only regulated **24 VDC**. Reverse protected. Never exceed 30 V. |
| **+5 V / +12 V (Bottom-right)** | Isolated sensor supply. Use for dry-contact sensors only. Protected by DC-DC and fuses. Not for powering relays or actuators. |

---

## ⏸ Inputs & Relays

| Interface | Warning |
| --- | --- |
| **Inputs I1–I5 (Top row)** | Opto-isolated channels. Connect only dry-contact or open-collector sources. Return via **GND (top right)** (this is **GND_ISO**, not logic ground). |
| **Relays (Bottom row)** | `NC / COM / NO` per relay. Dry contact only. Max: **3 A @ 250 VAC / 30 VDC**. Use snubbers for inductive loads (e.g. pumps, valves). |
| **Relay Power** | Relay contacts are **not powered**. External load must have its own power source. |

---

## 🔗 Communication & USB

| Interface | Warning |
| --- | --- |
| **RS‑485 A/B/COM (Bottom left)** | Use twisted pair for A/B. COM is signal ground. Protect against surges. Not suitable for long unshielded runs or outdoor wiring. |
| **USB‑C (Front panel)** | For **setup only** using Web Serial in Chrome/Edge. ESD protected. Not for field use or runtime connection. Disconnect after configuration. |

---

## 🔘 User Interface

| Element | Notes |
| --- | --- |
| **Buttons (U1–U4)** | Configurable: relay override, irrigation start/stop. Button press may override Modbus or automation logic. |
| **LEDs (U1–U4)** | Configurable for DI, Relay, or Irrigation indication. Driven from MCU via transistors. |

---

## 🛡 Shielding & EMC

| Area | Recommendation |
| --- | --- |
| **Cable Shielding** | Use shielded cable for RS‑485 and sensor lines. Terminate shield at controller end only. Avoid routing near motors/VFDs. |
| **Inductive Loads** | Use RC snubbers or TVS across relay contacts for solenoids, pumps, or coils. |

---

<a id="4-installation-quick-start"></a>

# System Architecture & Pinout

<div align="center">

<table>

<tr>

<td align="center">

<strong>System Block Diagram</strong><br>

<img src="Images/WLD_Diagram.png" alt="System Diagram" width="360">

</td>

<td align="center">

<strong>Terminal Map</strong><br>

<img src="Images/photo1.png" alt="Module Photo and Terminal Map" width="360">

</td>

</tr>

<tr>

<td align="center">

<strong>Field Board Layout</strong><br>

<img src="Images/FieldBoard_Diagram.png" alt="Field Board" width="360">

</td>

<td align="center">

<strong>MCU Board Layout</strong><br>

<img src="Images/MCUBoard_Diagram.png" alt="MCU Board" width="360">

</td>

</tr>

</table>

</div>

---

---

# ESPHome YAML Configuration & Hardware Pinout Manual

<div align="center">

<table>

<tr>

<td align="center">

<strong>System Block Diagram</strong><br>

<img src="Images/WLD_Diagram.png" alt="System Diagram" width="360">

</td>

<td align="center">

<strong>Terminal Map</strong><br>

<img src="Images/photo1.png" alt="Module Photo and Terminal Map" width="360">

</td>

</tr>

<tr>

<td align="center">

<strong>Field Board Layout</strong><br>

<img src="Images/FieldBoard_Diagram.png" alt="Field Board" width="360">

</td>

<td align="center">

<strong>MCU Board Layout</strong><br>

<img src="Images/MCUBoard_Diagram.png" alt="MCU Board" width="360">

</td>

</tr>

</table>

</div>

---

---

# Links

Arduino

C++

MicroPython