Datasheet

WLD-521-R1 — Water Meter & Leak Detection Module

Part No. TBD

# Product Description

The WLD-521-R1 is a configurable smart I/O module designed for leak detection, water flow metering, heat energy monitoring, and local irrigation control. It includes 5 opto-isolated digital inputs, 2 SPDT relays, and optional 4 buttons and 4 LEDs for manual control and local status indication. Configuration is performed via the WebConfig interface over USB-C (Web Serial).

# Technical Specifications

| Specification | Details |
| --- | --- |
| Digital Inputs | 5; Opto‑isolated inputs with MOSFET front‑ends, debouncing, and isolated return (GND_ISO); suitable for dry contacts or pulse flowmeters. |
| Analog Outputs | 0; — |
| Relays | 2; SPDT dry contacts (~3 A @ 250 VAC); driven via opto‑isolated stages and RC/snubber-protected. Terminals NO/COM/NC exposed. |
| 1‑Wire Bus | 1; Protected 3‑pin header (+5 V / DATA / GND) with level shifting and ESD protection; supports DS18B20 sensors. |
| LEDs | 4 user + status; 4 user LEDs controlled via transistor drivers; additional LEDs for power and RS‑485 TX/RX activity. |
| Buttons | 4; Front-panel tactile buttons connected to MCU GPIOs for relay override, irrigation control, and test functions. |
| Modbus RTU | Yes; RS‑485 transceiver with surge/bias/ESD protection and DE/RE control. Typical config: 19200 baud, 8N1. |
| USB‑C | Yes; Type-C port with ESD protection and Web Serial interface; used for configuration via WebConfig. |
| Power | 24 VDC; Fused, reverse-protected input. Internal buck regulator provides +5 V and +3.3 V. Isolated +5 V and +12 V rails available for sensor power. |
| MCU | RP2350A; Dual-core MCU with QSPI flash and 12 MHz crystal; SWD debug header available. |
| Protection | TVS, PTC, ESD; Multi-stage protection on RS‑485 and USB lines; isolated sensor rails; opto-isolated inputs; snubbers on relays. |
| V+ / 0V (Top-left) | Connect only regulated 24 VDC. Reverse protected. Never exceed 30 V. |
| +5 V / +12 V (Bottom-right) | Isolated sensor supply. Use for dry-contact sensors only. Protected by DC-DC and fuses. Not for powering relays or actuators. |
| Inputs I1–I5 (Top row) | Opto-isolated channels. Connect only dry-contact or open-collector sources. Return via GND (top right) (this is GND_ISO, not logic ground). |
| Relays (Bottom row) | `NC / COM / NO` per relay. Dry contact only. Max: 3 A @ 250 VAC / 30 VDC. Use snubbers for inductive loads (e.g. pumps, valves). |
| Relay Power | Relay contacts are not powered. External load must have its own power source. |
| RS‑485 A/B/COM (Bottom left) | Use twisted pair for A/B. COM is signal ground. Protect against surges. Not suitable for long unshielded runs or outdoor wiring. |
| USB‑C (Front panel) | For setup only using Web Serial in Chrome/Edge. ESD protected. Not for field use or runtime connection. Disconnect after configuration. |
| Address | 3 |
| Baudrate | 19200 |
| Format | 8N1 |
| Relay Outputs | 2; SPDT dry contact (NO/C/NC); snubbered; local/Modbus/logic control. |
| User LEDs | 4; Configurable (Solid/Blink) for DI/Relay/Irrigation/Override feedback. |
| User Buttons | 4; Assignable actions (Relay toggle/pulse, Override, Irrigation start/stop). |
| RS‑485 (Modbus) | 1; Half‑duplex multi‑drop; A/B/COM terminals; fail‑safe & surge‑protected. |
| Sensor Power | 2; Isolated +12 V / +5 V rails for low‑power sensors only (fused, filtered). |
| Supply voltage (V+) | 20 V / 24 V / 30 V / SELV; reverse/surge protected input. |
| Power consumption | — / 1.85 W / 3.0 W / Module only (no external loads). |
| Logic rails | — / 5 V / 3.3 V / — / Buck + LDO derived. |
| Isolated sensor rails | — / +12 V ISO / +5 V ISO / — / Fused, LC‑filtered; for sensors only (≤ ~150 mA shared). |
| 1‑Wire bus power | — / +5 V (logic) / — / Non‑isolated, for 1‑Wire devices only. |
| Type | Opto‑isolated; dry contact / open‑collector / pulse. |
| Threshold | Low‑voltage, sensor‑level (use GND_ISO return). |
| Debounce | Firmware‑controlled. |
| Pulse rate (counter) | ~ up to 9–10 Hz practical for flow meters. |
| Isolation | Field domain to logic via opto barrier. |
| Ratings (contacts) | 250 VAC 16 A (cosφ=1), 250 VAC 9 A (cosφ=0.4), 30 VDC 10 A. |
| Recommendation | Use coupling relays for inductive or >5 A continuous loads. |
| RS‑485 | Modbus RTU, half‑duplex; 9600–115200 bps (default 19200, 8N1); fail‑safe, short‑circuit limited, surge‑protected. |
| Operating temperature | 0…40 °C |
| Humidity | ≤95 % RH, non‑condensing |
| Ingress / Safety class | IP20; Operation Type 1 |
| Rated impulse (outputs) | 2.5 kV |
| Max altitude / pollution | 2000 m / Degree 2 |
| Digital inputs | — / — / — / Opto‑isolated; per‑channel surge protection. |
| Relay contacts (R1–R2) | — / — / 250 VAC 16 A / 30 VDC 10 A / Use external snubbers; derate for inductive loads. |
| RS‑485 interface | — / 115200 bps / — / Half‑duplex; fail‑safe; short‑circuit limited; surge‑protected. |
| Interface | RS‑485 (half-duplex) |
| Parity | 8N1 |
| Role | Slave (responds to master requests) |
| Supported FCs | `0x01` Read Coils, `0x02` Read Discrete Inputs, `0x03` Read Holding, `0x04` Read Input, `0x05/0x0F` Write Coils, `0x06/0x10` Write Holding |

# Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type / pitch | terminal torque, polarity, and RS‑485 A/B wiring. Use 120 Ω resistors and surge protectors if needed. ¦ |
| Environmental Ratings | Operating temperature | Operating temp |
| Environmental Ratings | Ingress protection | IP20 |
| Environmental Ratings | Relative humidity | Humidity ¦ ≤95 % RH, |
| Mechanical & Packaging | Product dimensions | Not specified in README |
| Mechanical & Packaging | Mounting | 35 mm DIN |
| Mechanical & Packaging | Net weight | 0 kg |

# Compliance & Certifications

ce

ee

ce

ce

CE

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ee

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ee

ee

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ce

ee

ce

ce

ce

ce

ce

ee

ee

ce

ce

ce

ee

ce

ce

ce

ee

ee

ce

ce

ce

ce

ce

ee

ee

ce

ee

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

ce

CE

ee

ee

Safety notice: This module is intended for SELV/PELV applications. Install and wire according to local regulations. Do not connect mains to logic/input terminals unless so specified.

# Published by

ISYSTEMS AUTOMATION S.R.L.
Deligintei 18
Ploiesti
Romania
Tel: +40721389963
http://www.home-master.eu