Datasheet

ESP32 MiniPLC

Part No. 0000001

## Product Description

The HomeMaster MiniPLC is a professional, open-source DIN rail controller built around the ESP32 platform, designed for robust and scalable smart automation in residential, commercial, and light industrial environments. It combines extensive onboard I/O—including relays, digital and analog inputs, temperature sensors, and a user interface—with native Home Assistant integration via pre-installed ESPHome.

Engineered for reliability and flexibility, the MiniPLC supports multiple power input options (24V DC or wide-range AC/DC) and features an isolated RS-485 Modbus interface for expansion with a wide range of compatible I/O modules. Its local processing capability ensures continued operation even when network or cloud connectivity is lost, making it suitable for mission-critical applications.

This controller operates as a complete standalone automation system using its comprehensive onboard I/O, while also offering seamless expansion via the RS-485 bus to connect HomeMaster smart modules for energy metering, lighting control, security, and more. It provides a versatile, ready-to-integrate platform for HVAC control, energy management, security systems, lighting automation, and custom industrial applications.

## Technical Specifications

| Specification | Details |
| --- | --- |
| Microcontroller | ESP32-WROOM-32U (dual-core) |
| Power Input | 24 V DC nominal (V+ / 0V) OR 85–265 V AC (L / N) OR 120–370 V DC (L / N + / −) |
| Digital Inputs | 4 × isolated, 24 V DC compatible |
| Relay Outputs | 6 × SPDT — 3 A MAX continuous per output (board/system limit). Relay component contacts rated up to 12 A @ 250 V AC (resistive). |
| Analog Inputs | 4 × 0–10 V, 16-bit (ADS1115) |
| Analog Output | 1 × 0–10 V, 12-bit (MCP4725) |
| Temperature Inputs | 2 × RTD (PT100/PT1000 via MAX31865), 2 × 1-Wire (DS18B20 compatible) |
| Display | 128 × 64 OLED (SH1106) |
| User Interface | 4 buttons, 3 user LEDs, 1 status LED, onboard buzzer (GPIO2, PWM) |
| Wi-Fi | Wi-Fi (ESP32) |
| Ethernet | Optional Ethernet (LAN8720 PHY) |
| RS-485 | RS-485 Modbus RTU (MAX485, half-duplex) with TVS surge protection, PTC fuses, EMI choke, and fail-safe biasing |
| Storage | MicroSD card (SPI interface, power-switched 3.3 V rail) |
| USB | USB-C (ESD protected, CC detection, data to ESP32) |
| RTC | PCF8563 with battery backup |

Note: Relay outputs are not internally fused. Use external overcurrent protection per local code and use an external contactor/relay for loads above 3 A or with high inrush/inductive characteristics.

## Installation, Environmental & Mechanical

| Category | Specification | Details |
| --- | --- | --- |
| Terminal Specifications | Terminal type | Pluggable screw terminal blocks, 5.08 mm pitch |
|  | Terminal pitch | 5.08 mm |
|  | Wire cross-section | 0.2–2.5 mm² (AWG 24–12) |
|  | Conductor type | Solid or stranded copper |
|  | Stranded wire | Ferrules recommended |
|  | Tightening torque | 0.4 Nm (max) |
| Environmental Ratings | Operating temperature | 0 °C to +40 °C |
|  | Storage temperature | -10 °C to 55 °C |
|  | Relative humidity | 0–90 % RH, non-condensing |
|  | Ingress protection | IP20 (inside cabinet) |
|  | Installation | Indoor control cabinet only; not for outdoor or exposed installation |
|  | Terminal protection | All wiring terminals must be protected against accidental contact |
| Mechanical & Packaging | Product dimensions | 157.4 × 91 × 58.4 mm (6.2 × 3.58 × 2.3 in) (L × W × H) |
|  | DIN units | 9 division units (≈ 90 mm DIN rail mounting width) |
|  | Mounting | 35 mm DIN rail |
|  | Net weight | 300 g |
|  | Gross weight | 450 g |
|  | Pack size | 230 × 140 × 87 mm (9 × 5.5 × 3.4 in) (L × W × H) |
|  | Mechanical drawing | Front + side views with DIN-clip depth (see below) |
|  | Notes | All dimensions shown in millimeters unless stated otherwise |

Install only inside a control cabinet with ventilation; the cabinet must include a protective front plate covering all module connection terminals and a closing protective door; not for outdoor or exposed installation.

All wiring terminals must be protected against accidental contact by an insulating front plate, wiring duct, or terminal cover. Exposed live terminals are not permitted.

### Cable Recommendations & Shield Grounding

This section applies to Analog (0–10V), Temperature (RTD / 1-Wire), and RS-485. Use shielded, twisted constructions and bond shields correctly to reduce EMI and ground-loop issues.

#### General Routing Rules

- Route low-level signal cables (Analog/RTD/1-Wire/RS-485) separately from mains, relay outputs, contactors, VFD motor cables, and power wiring.

- If crossing power cables is unavoidable, cross at 90°.

- Keep cable runs as short as practical and avoid parallel runs with high-current conductors.

#### Analog (0–10V) Cable

- Construction: twisted pair (Signal + GND) per channel

- Shielding: overall shield (standard) or individually shielded pairs (high-EMI)

- Examples: J-Y(ST)Y (overall shield) or LI2YCY PIMF (shielded twisted pairs; one pair per channel)

#### Temperature Cable

##### RTD (PT100/PT1000)

- Recommended: shielded multi-core for 2/3-wire; shielded pairs for best accuracy (4-wire)

- Examples: J-Y(ST)Y (overall shield) or LI2YCY PIMF (pairs; e.g. 2×2×0.50 for 4-wire)

##### 1-Wire (DS18B20)

- Recommended: shielded 3-core ( +5V / DATA / GND ) for typical installations

- High-EMI / long runs: shielded pairs + overall shield (e.g. LI2YCY PIMF 2×2×0.50)

- Topology: daisy-chain (bus). Avoid star wiring.

- Stubs: keep sensor stubs ≤ 0.5 m.

- Pull-up (DATA): 4.7 kΩ typical; 2.2–3.3 kΩ for long/heavy loads.

#### RS-485 Cable

- Construction: twisted pair for A/B

- Characteristic impedance: 120 Ω (recommended)

- Shielding: overall shield is recommended in cabinets; use individually shielded pairs + overall shield in high-EMI

- Examples: J-Y(ST)Y 2×2×0.5 mm² or LI2YCY PiMF 2×2×0.50

- Use one twisted pair for A/B. Use the second pair for COM (0V reference) or spare.

#### Shield Grounding

- Default recommendation: bond cable shield(s) to cabinet PE/EMC ground at the PLC end only.

- Do not connect shields to signal terminals (AI/AO/RTD/1-Wire/RS-485 A/B/COM).

- If both ends are in equipotential bonded cabinets, shields may be bonded at both ends using proper 360° clamps.

Published by

ISYSTEMS AUTOMATION S.R.L.

Deligintei 18, Ploiesti, Romania

Tel: +40721389963

http://www.home-master.eu